## Instructions
The UCL Mini Ska template is a self-assessment tool for use on smaller fit-out projects which are of limited scope and budget (generally up to a maximum of £2m). Examples include small-scale engineering projects, minor refurbishment work, redecoration or lighting upgrades. This version also covers smaller lab fit-out projects (e.g. individual lab fit-out, <£2m) - these requirements are ADDITIONAL to the standard Mini-Ska items. Larger fit-out projects should be assessed using the full RICS Ska methodology. Major refurbishments and new build projects generally fall under BREEAM. All relevant 'in scope' criteria must be achieved wherever practical AND unless otherwise agreed with UCL Estates.
The criteria listed should be copied directly into relevant specification and tender documentation.
For each separate Mini-Ska measure, the UPO/ project manager is responsible for confirming the following information:
In scope | Included in design | Achieved on site | Validation | References
Is the measure relevant to the scope of works for the project? | If so, have each of the requirements been fully allowed for in design and tender documentation? | (On completion of the works) Were each of the measures implemented as designed/ specified? | Provide a brief explanation of how each requirement will be/ was implemented | Provide a list/ locations of documentary evidence which can be used to confirm compliance
The lists referenced can readily be found and searched online:
Energy Technology List | https://etl.beis.gov.uk/
BRE Green Guide | https://www.bre.co.uk/greenguide
Green Book Live | http://www.greenbooklive.com
For further information or support using this tool, please contact the UCL Sustainability Team:
Green UCL | sustainableucl@ucl.ac.uk
Ben Stubbs | b.stubbs@ucl.ac.uk |  |  | V2.1 2020-12-15

## Mini-Ska
ID | Category | Measure | Requirements | In scope? | Included in design | Achieved on site | Validation | Evidence
Have you incorporated all relevant requirements into relevant specifications/ tender documents? | [6 empty] | Please select to confirm
MS01 | Energy & CO2 | Efficient Lighting | Where changes/ upgrades are being made to lighting systems: 1. Confirm how design features have minimised the need for artificial lighting, wherever possible (e.g. by maximising daylight) 2. All new individual lamps and light fittings (luminaires) must use LED technology as standard. 3. All new general lighting systems (i.e. >20m2 and 300-500 lux) shall be designed to achieve a maximum load of 7W/m2. 4. All new installations are to be automatically controlled for daylight and occupancy, as appropriate. Spaces with natural daylight should be provided with manual on/off switches and absence detectors. 5. Where possible, include task lighting for specific lab activity as opposed to increasing lighting levels for the whole lab. 6. Information on the operation of new controls/ systems must be clearly communicated to relevant building users.
MS02 | Energy & CO2 | Sub-metering | Where major work to mechanical, electrical or water supply systems is being carried out: 1. Automatic monitoring and targeting (AMT) equipment is to be installed. AMT equipment comprises meters, an automatic meter reading device and analytical software. 2. Equipment must be linked to: • For heat, gas and water meters - the UCL BMS. • For electricity meters - the UCL ION Enterprise system 3. Sub-meters are to be installed for relevant zones within the fit-out area and/or high consuming energy items, as appropriate. 4. All meters must be commissioned onto UCL's BMS/ION Enterprise system prior to handover.
MS03 | Energy & CO2 | Connection to district heating network and chilled water systems | For projects involving heating/cooling system modifications: 1. Larger projects must carry out energy modelling to ascertain any increased energy demand. 2. Where feasible, the priority is to always connect to the district heating network for heating and an existing chilled water system for cooling. Follow the District Heating Connection standard available on UCL's Employer's Requirements page. 3. Derogations from this approach must be discussed/ agreed with the UCL energy team.
MS04 | Energy & CO2 | Boiler replacement | Where boilers are being upgraded or replaced: 1. The project team must carry out an options appraisal with a view to reducing life cycle costs and carbon emissions. 2. New boilers are on the Energy Technology List (ETL) or meet/ exceed ETL criteria. Speak to UCL the energy team for further information.
MS05 | Energy & CO2 | Domestic Hot Water (DHW) | Where dedicated DHW systems are being upgraded or replaced (i.e. separate from space heating): 1. Gas-fuelled DHW systems are on the Energy Technology List (ETL). 2. Electricity-fuelled DHW systems should only be used where connection to the main building system is not possible/ practical. Where required, they must have a standing heat loss better than that specified in table 5 of BS EN 15450:2007 This measure excludes electric heaters that have a storage capacity of less than 30 litres
MS06 | Energy & CO2 | Heating, ventilation and air conditioning (HVAC) controls | Where HVAC systems are being provided, upgraded or replaced: 1. Options for designing out or minimising new mechanical plant have been considered. Prioritise passive design features. 2. All new heating and cooling systems must be fully controlled via the Building Management System (where present). This must include the ability to change set-points and time schedules. 3. Where heating and cooling is provided by different systems in the same space they should be interlocked to prevent simultaneous operation. 4. Heating, cooling and ventilation should be controlled via a form of occupancy detection (either CO2 sensors for large spaces or presence detection for cellular offices). 5. Where appropriate (e.g. cellular offices, lab spaces) users should be provided with HVAC controls limited to +/- 1.5°C of the set point. 6. Systems should be programmed for set-points and time-schedules in line with UCL's Heating, Cooling and Ventilation policy.
MS07 | Energy & CO2 | Efficient Equipment | Where new electrical/ electronic equipment is required: 1. Options for the reuse of equipment from within UCL are prioritised wherever feasible. 2. Waste equipment must be disposed of in accordance with relevant UCL guidelines set out at: https://www.ucl.ac.uk/greenucl/what-we-do/waste-and-recycling 3. Any new equipment must meet the following energy efficiency requirements, as relevant: • White Goods: refer to UCL White Goods Procurement Policy (e.g. A+ rated fridges/ freezers) • Other small power/ plug in equipment: Energy Star rating and/ or Government Buying Standards • Kitchen/ catering facilities: follow CIBSE TM50 guidance
MS08 | Energy & CO2 | Energy efficient hand-dryers | 1. Paper towel dispensers must not be specified for standard washrooms unless functional requirements dictate. 2. Paper towel dispenser may be provided alongside hand dryers in accessible facilities. 3. All new electrically-operated hand-dryers are either: • 'Biodrier Eco' (www.biodrier.com); or • have equivalent energy performance and noise rating; or • have been awarded a carbon reduction label by The Carbon Trust.
MS09 | Materials | Timber | Where timber or timber-derived products are specified: 1. 100% of timber used must be either: • reused/ reclaimed; or • all new timber must be supplied with a Chain of Custody (CoC) from one of the following forest certification schemes only: - Forest Stewardship Council (FSC) - Programme for the Endorsement of Forest Certification (PEFC) - Grown in Britain certification (GiB)
MS10 | Materials | Flooring | Where floor finishes are being upgraded or replaced: 1. Options for reuse or recycling of existing floor finishes must be prioritised. Consider exposing/ restoring any covered floors (e.g. parquet). 2. Use supplier take back schemes for waste flooring, where available. 3. All new floor coverings must meet at least one of the following criteria: • if new, are manufactured with 25% recycled content for hard flooring or 50% recycled or renewable/natural content for soft flooring • have an A or A+ rating in BRE’s The Green Guide to Specification/ Green Book Live database • carpets are installed as part of a manufacturer’s recycling or ‘take back’ scheme and labelled accordingly 3. In addition, ALL timber, must meet the criteria of good practice measure MS09 Timber.
MS11 | Materials | Furniture (e.g. workstations, tables, chairs, storage units) | Where furniture items are planned to be replaced: 1. All reasonable options for reuse/ repair in situ have been exhausted 2. Raise a request with the UCL Relocation, Moves and Decants team at least 2 weeks in advance of any planned moves to ensure: a) Adequate arrangements are made for the storage or reuse of any redundant, but reusable, items b) Existing UCL inventory must be checked with a view to reusing items from storage/ other projects 3. Any new items meet at least one of the following criteria: • the company manufacturing the products is certified under the Furniture Industry Sustainability Programme (FISP) scheme; • items are manufactured with at least 80% recycled content (measured by mass) and 100% recyclable content, designed for deconstruction with components that can be recycled. • have been awarded the EU Ecolabel 4. In addition, ALL timber, must meet the criteria of good practice measure MS09 Timber.
MS12 | Materials | Other Materials: Circular Economy | For projects involving significant use of other materials (e.g. ceiling systems; partitions; window frames; door sets; blockwork; kitchen fittings; countertops): 1. Confirm how materials used as part of the fit-out achieve one or more of the following: • reused or reclaimed; • higher levels of recycled content • have an A or A+ rating in BRE’s The Green Guide to Specification; • demountable and reusable systems • supplied with Cradle to Cradle certification (silver-platinum)
MS13 | Waste | Construction waste planning and recycling | All projects: 1. Carry out an audit of materials likely to be stripped out/ disposed of as part of the project with a view to minimising waste and maximising residual value. 2. Waste management must be planned and documented in accordance with the waste hierarchy (i.e. in order of priority: reduce - reuse - recycle - recover - dispose). 3. Projects generating significant quantities of waste must prepare a resource (site waste) management plan prior to the construction phase. Note: Waste reports must be recorded and broken down by waste steam and show that at least 90% of waste produced on site is diverted from landfill.
MS14 | Waste | Operational waste facilities | For projects leading to variations in waste types/ volumes: 1. Demonstrate that adequate new facilities have been provided to assist with waste management, segregation and recycling. Any new bins must be approved by the UCL Waste Manager. 2. Carry out a risk assessment for any new waste streams.
MS15 | Water | Water-efficient sanitary equipment | Where sanitary equipment is being upgraded or replaced in individual or communal washrooms: 1. Target an effective WC flush volume of 4.5 litres or less, subject to local drainage infrastructure. Existing systems should be retrofitted where practical. Note: 4.5 litre effective flush volume can be achieved by a 6l/ 4l dual flush which is generally sufficient for most UCL facilities. Some core campus drainage may not be able to support lower flush volumes than this. 2. Flow rate on taps should be limited to 4 litres/minute up to a pressure of 5 bar (through new taps or retrofitting flow control devices) 3. Install automatic taps (e.g. infrared) with a standard shut-off after max. 3 seconds. 4. Flow rate for showers is to be limited to max. 8 litres/minute up to a pressure of 5 bar. 5. Install flow control devices to isolate the cold water supply to washrooms when unoccupied (to minimise water leaks and wastage). This usually comprises a solenoid valve linked to occupancy sensor, which may also serve lighting. The shut-off system only needs to be applied to the cold water supply for taps, WCs and urinals (not showers).
MS16 | Wellbeing | Daylight and glare control | For occupied spaces with workstations and windows/ rooflights: 1. Design space to maximise natural daylight opportunities (with due regard for specailst functions, photo-sensitive materials etc). 2. Occupant-controlled window coverings (typically blinds or screens) must be fitted to the external windows to minimise glare and allow the best possible retention of views out. 3. Fabric screens, where specified, should have a visual light transmittance (VLT) of less than 10%. Use black-out blinds where necessary.
MS17 | Wellbeing | Thermal comfort | Where changes are being made to thermal envelope (e.g. windows/ façade) or HVAC systems: 1. Confirm how building users have been consulted in relation to thermal comfort within the existing space. 2. Demonstrate how thermal comfort can be maintained or, ideally, improved with due regard for: a) Positioning of furniture in relation to cold/ hot spots (e.g. from HVAC equipment locations, draughts, radiant temperatures etc). b) UCL Heating, Cooling and Ventilation Policy.
MS18 | Wellbeing | Harmful emissions from construction products | Where the internal fit-out includes any of the products/ materials listed below: 1. Options with low emissions levels must be specified for the following (target ≤ 0.06 mg/m³ for formaldehyde; ≤ 1.0 mg/m³ for total volatile organic compounds): • Interior paints and coatings • Wood-based products, including wood flooring (e.g. MDF, plywood, acoustic board etc) • Flooring materials (e.g. levelling compounds; resin flooring) • Ceiling, wall, and acoustic and thermal insulation materials • Interior adhesives and sealants
Further guidance on relevant standards is available here.
MS19 | Pollution | Refrigerants | Where cooling systems are being specified, upgraded or replaced: 1. Refrigerants used in systems must have an Ozone Depleting Potential (ODP) of zero (e.g. HFCs) and with the lowest feasible Global Warming Potential (GWP), unless otherwise agreed. 2. Where the value of the cooling systems is under £10,000 simply confirm the refrigerants selected. Note: R32 will meet this requirement.
MS20 | Other | Occupant guidance & instructions (Building User Guide) | Where building services or AV equipment have been provided or upgraded: 1. Clear, non-technical guidance must be provided in relation to the operation and environmental performance of the space, with a view to optimising energy efficiency and user comfort (separate from O&M). 2. This information should be added to any existing Buiding User Guide for the building. Note: Precise format/ content will vary according to the facilities or equipment. For smaller projects appropriate signage or desk top guides may be sufficient.
MS21 | Other | Commissioning | For all projects involving the specification, upgrade or replacement of building services: 1. New systems are to be commissioned, or existing systems recommissioned, in accordance with CIBSE & BSRIA guidance 2. Provide updated commissioning records/documentation to confirm that the building has been fine-tuned and seasonal commissioning of complex equipment has been undertaken.
Yes | Yes
No | No
N/A
Please select to confirm
Yes
No
Note on D2: All relevant requirements must be accounted for. Derogations to be agreed with UCL Sustainability.
Note on E2: Is this measure relevant to the scope of works for the project?
Note on F2: Have each of the requirements been allowed for in design and procurement documentation?
Note on G2: Were each of the measures implemented as designed? Confirm on project completion
Note on H2: Provide a brief explanation of how each requirement will be/ was implemented
Note on I2: Provide a list of documentary evidence which can be used to confirm compliance and state where this can be found
Note on D8: A copy of the relevant requirements from BS EN 15450:2007 is available in the full Ska HE Standard, available at: http://www.rics.org/uk/knowledge/ska-rating-/ska-he/
Note on D9: UCL Heating, Cooling and Ventilation Policy available at: www.ucl.ac.uk/greenucl/heating
Note on D10: A copy of the UCL White Goods Procurement Policy is available at: https://www.ucl.ac.uk/greenucl/sites/greenucl/files/ucl_white_goods_purchasing_guide_.pdf
Note on D20: UCL Heating, Cooling and Ventilation Policy available at: www.ucl.ac.uk/greenucl/heating

## Ska-Labs
ID | Category | Measure | Requirements | In scope? | Included in design | Achieved on site | Validation | Evidence
Have you incorporated all relevant requirements into relevant specifications/ tender documents? | [6 empty] | Please select to confirm
MSL01 | Project Management | User Consultation | 1. The installation or refurbishment of one or more of the following must involve prior consultation with relevant departmental representatives to ensure that the proposed solution is appropriate, energy efficient and fit for purpose: • ULT freezers • Fume cupboards • Class II safety cabinets • Specialist waste streams • Chemical stores
MSL02 | Project Management | Equipment procurement | Confirm how the following procurement guidlines have been addressed/ incorporated when purchasing new equipment: 1. UCL Lab Procurement Guidance. Approved suppliers must be used. 2. Consult with other users with a view to sharing equipment wherever feasible. 3. Laboratories which are purchasing generic new equipment must account for life cycle costs including energy consumption, maintenance and replacement (e.g. ULT freezers, safety cabinets, drying cabinets, and autoclaves).
MSL03 | Project Management | Air Flow - Future Proofing | 1. Demonstrate how potential future increases in extract requirements have been accounted for in the sizing of ventilation systems (i.e. to accommodate changes in activities and/ or number of lab users). 2. Prioritise re-circulating safety cabinets over ducted models. Provide clear justification where ducted models are required. 3. Replacement of ducted with re-circulating safety cabinets must account for increased heat loads and implications for decontamination procedures.
MSL04 | Project Management | User Guidance | 1. Provide a user guide that includes advice on sustainable lab practices including energy, water, materials and waste management. This should be delivered/defined as per the compulsory training outlined in HSE CGS 201. 2. Where available for the building, this information may be added to an existing UCL Building User Guide. (Template available at: https://www.ucl.ac.uk/estates/policies/2019/dec/building-user-guide). 3. Ensure all local controls and relevant mechanics have appropriate guidance for current and future users (e.g. what closing the sash does, possible alarm triggers, what all lights/buttons/symbols do, etc.).
MSL05 | Energy & Safety | Air change selection | 1. Demonstrate how safe room air change rates (ACH) have been achieved with due regard for occupancy, energy efficiency and fume cupboard demand. Note: CIBSE Guide B recommends a broad range of 6-15 ACH for laboratories 2. Indicate what ACH has been selected, and provide rationale.
MSL06 | Energy & Safety | Air change reduction | 1. One of the following options for room ACH savings should be employed: a) Demand driven ventilation using CO2 sensors where the occupancy ventilation rate is higher than other ventilation rate requirements. b) Reducing air change rates and room temperature range via night time setbacks during unoccupied hours. Note: 24/7 ACH based on full occupancyare rarely necessary. HVAC zoning may be required to achieve maximum savings from setbacks (e.g. between offices and labs).
MSL07 | Energy & Safety | Air change reduction: BSUs | Subject to appropriate environmental conditions being achieved: 1. Reduce BSU ACH where only individually ventilated cages (IVCs) have been installed, and subject to Home Office approval. Note: As a guide: ACH should be 12 (+/-2 ACH) in facilities with IVCs and rooms where animals are not exposed (now permissible subject to Home Office consultation). 2. Engage with Home Office officers prior to any ventilation balancing.
MSL08 | Energy & Safety | HVAC: Heat recovery | 1. Recover energy from ventilation extracts wherever feasible (use corrosion resistant heat recovery coils). 2. Ensure adequate separation of intakes and extracts to avoid recycling of polluted/ stale air in accordance with BS EN 13779:2007 Annex 2. 3. Incorporate suitable filtration to minimise external air pollution, as defined in BS EN 16798-3:2017.
MSL09 | Energy & Safety | Air Balancing | 1. Demonstrate how building-wide ventilation systems have been taken into account, and how any negative impacts of proposed modifications will be mitigated. 2. Undertake rebalancing exercises where necessary.
MSL10 | Energy & Safety | Equipment Cooling Strategy | 1. Demonstrate how the impact of equipment heat load on cooling requirements has been taken into account and mitigated (e.g. freezers). 2. Confirm that any controls or sensors are not near heat outputs. 3. Passive cooling strategies should be prioritised within recommended operational limits of equipment and in accordance with UCL Heating & Cooling Policy (i.e. with due regard for thermal comfort). https://www.ucl.ac.uk/greenucl/ucl-heating-cooling-and-ventilation-policy 4. Dedicated freezer rooms should be prioritised for 3 or more freezers and should target 18-20C to optimise operational efficiency. Mechanical cooling may be required above 22C.
MSL11 | Energy & Safety | Higher Equipment Loads | 1. Notify installation of any equipment with 3-phase power; excess cooling/heating, water or drainage requirements; or other specialist requirements with excess loads to UCL Estates. 2. Investigate the potential for removal of 3-phase power capacity where no longer needed.
MSL12 | Energy & Safety | Fume Cupboard Specification: Air Flow | 1. Variable air volume (VAV) fume cupboards should be installed where they will lead to overall energy reductions (e.g. particularly in rooms with multiple fume cupboards): • Consideration must be given to room ACH requirements, as well as heating & cooling (modulating extract rates may affect these). • Any variations in maintenance requirements should be communicated to UCL Estates, H&S, and Sustainability. • Provide clear justification where VAV has not been selected.
MSL13 | Energy & Safety | Fume Cupboard Specification: Face Velocity | 1. For low velocity fume cupboards, target average face velocities of 0.35ms at 500mm for normal activities and where risk assessment permits. • Ensure sufficient containment in compliance with test requirements of BS EN 14175. • Low velocity (0.35-0.4ms) F/Cs must be validated by manufacturers via containment testing and also prior to usage. • Confirm that any infringements of airflow have been effectively considered and mitigated (e.g. air conditioning/ fans etc). Note: Higher face velocities are required for constant air volume (CAV) fume cupboards, and for work involving radioactive or highly toxic substances. Please refer to detailed guidance from UCL Safety Services: https://www.ucl.ac.uk/safety-services/a-z/lev/fume-cupboards
MSL14 | Energy & Safety | Fume Cupboard Specification: Sash Design | 1. For VAV fume cupboards, specify default sash heights of 400mm - ensuring that this can be overriden and raised to 500mm for testing purposes, taller users and setting up. This may be achieved using sash locks and/ or alarms. 2. For both VAV and CAV fume cupboards, target narrower models where feasible to further minimise energy usage. Note: In all cases health, safety and welfare must take priority. User input and risk assessments must be reviewed and adhered to when setting sash heights. Note: For CAV fume cupboards the default sash height shall remain at 500mm as varying the sash height does not impact on energy usage. Note: Setting sash heights at 400mm rather than 500mm can result in energy savings of 20%. However, testing must always be carried out at 500mm where fume cupboards open to this level.
MSL15 | Energy & Safety | Fume Cupboard Specification: Monitoring & Setback | VAV fume cupboards only: 1. Install passive infrared monitoring linked to automatic sash closures to set back air volume in absence of users. 2. Any sashes with auto-closure functionality should have handles removed to avoid users breaking units. Appropriate training and signage must be provided. Note: This requirement only applies to VAV fume cupboards, as fixed flow units should not have automatic sash closure unless requested specifically for health & safety reasons.
MSL16 | Energy & Safety | Ventilated storage | Fume cupboard chambers must not solely be used for longer term storage: 1. Engage users to determine if the provision vented storage cabinets can minimise the size and/ or number of fume cupboards. Note: Fume cupboards can use as much energy as the average family house.
MSL17 | Energy & Safety | Cold Rooms | 1. The installation or refurbishment of any new cold rooms (4C or colder) is to be avoided due to high energy consumption and maintenance costs; and impacts on business continuity in the event of compressor failures: • Provide designated rooms with separated refrigeration wherever feasible. • Otherwise provide clear justification as to why cold rooms are essential.
MSL18 | Waste | Lab Waste & Recycling | 1. Provide receptacles and space for a minimum 3 waste streams, with non-hazardous waste streams separated physically from hazardous/clinical waste. 2. Ensure that clear labelling is provided (available from UCL Sustainability). 3. Additional separate provision should be provided where significant specialist waste streams are present. For example, glass winchester recycling, tip-box recycling, sharps, packaging returns.
MSL19 | Waste | Single Use Plastics | 1. Provide a separate glass washer (and potentially dryer) where this has the potential to significantly reduce single-use plastics. 2. Confirm alternative arrangements to reduce single-use plastics, where applicable.
MSL20 | Water | Sink sizing and necessity | 1. Recirculating chillers must be prioritised for cooling requirements where taps/ sinks might otherwise be used. 2. Reduce sink sizes where possible to minimise the volume of 'soaking' for glassware, ensuring that larger can be accommodated where necessary.
MSL21
MSL22
MSL23 | Please select to confirm | Yes
MSL24 | Yes | No
MSL25 | No | N/A
Note on D2: All relevant requirements must be accounted for. Derogations to be agreed with UCL Sustainability. Note that Labs requirements are additional to basic Mini-Ska items
Note on E2: Is this measure relevant to the scope of works for the project?
Note on F2: Have each of the requirements been allowed for in design and procurement documentation?
Note on G2: Were each of the measures implemented as designed? Confirm on project completion
Note on H2: Provide a brief explanation of how each requirement will be/ was implemented
Note on I2: Provide a list of documentary evidence which can be used to confirm compliance and state where this can be found