## PSO Stage Fire Safety Checks
PROJECT FIRE SAFETY REQUIREMENTS
Based on the Bloomsbury Campus Masterplan Fire Strategy & UCL Mandatory Instruction 02 Construction Fire Safety Guidance for UCL Projects (Rev 9 - Oct 2015)
Unique Project Ref: |  | PS000000 | PS00057 | PS00057
Project Title: |  | xxxxx | UCL/RNOH – Biomedical Engineering Hub (BEH) | UCL/RNOH – Biomedical Engineering Hub (BEH)
Building Number: |  | 0 | INST OF ORTH - GOAT HOUSE_273 | INST OF ORTH - GOAT HOUSE_273
Building: |  | xxxxx | UCL/RNOH – Biomedical Engineering Hub (BEH) | UCL/RNOH – Biomedical Engineering Hub (BEH)
UCL Project Officer (UPO): |  | xxxxx
Project Manager (External) / Lead Designer / CDM: |  | xxxxx
For The Period Up To: |  | (insert date)
Fire Safety Technical notes available to download from www.ucl.ac.uk/fire/documents
1 | Stage 2 (B & C): Initiation (To be reviewed at each stage) |  | Yes | No
1.1 | Has the UCL Fire Safety Manager been provided with a Project overview?
1.2 | If new building / property acquisition - has fire safety due diligence survey been undertaken?
1.3 | Has a Stage 2/C fire strategy and/or fire risk assessment been developed based on the project brief?
1.4 | Is the project increasing the premises occupancy level? If Yes, has an initial stair and floor occupancy calculations been undertaken?
1.5 | Is Fire Engineering support required with a need to appoint Consultants, due to complexity? (Discuss first with UCL Fire Safety Manager)
1.6 | Has UCL Fire Safety Employers' Requirements (UCL Fire Safety Technical Notes) been issued to the Architect & MEP design team?
2 | Stage 3 (D & E): Project Design Development (To be reviewed at each stage) |  | Yes | No
2.1 | Will the Project be undertaken with UCL staff, students & visitors in occupation during building works - is a decant phasing programming or strategy provided for scheme and during works to include potential impact on surrounding buildings (fire spread, evacuation etc.) to ensure safety of occupants - If YES Design Team to work through impact assessments & provide details and mitigation in project fire risk assessment / fire strategy provision for consideration by Principle Contractor when tendering
2.2 | Are fire fighting shafts and other fire brigade facilities required or need to been considered?
2.3 | Are fire sprinklers required or need to been considered?
2.4 | Has an Evacuation Lift been considered as part of the inclusive design & MEP strategy? Separate sprinklers and from fire fighting facilities - Refer to fire fighting shafts / lifts rather than just lifts and more encompassing.
2.5 | Has there been consultation with a Fire Engineer (if provided), Building Control & UCL Fire Safety Manager by the Architectural design team?
2.6 | Has there been consultation with the Fire Engineer (if provided), Building Control & UCL Fire Safety Manager by the M&E / MEP design team?
2.7 | Has a 'Stage 3/D' fire strategy report been published?
3 | Stage 4 (F/G/H): Procurement & Planning (To be reviewed at each stage) |  | Yes | No
3.1. | All Contracts - has the required fire safety instructions been issued with tender documentation including named fire safety point of contact, fire strategy, fire phasing & mitigation docs and mandatory passive fire protection and fire stopping required through UCL framework contractor (UCL Fire MI06/TN066), Fire & Safety of Hoardings (MI07) and UCL Waste Management (fire safety) requirements (MI08).
3.2 | D&B Contract - has there been consultation with Appointed Contractor's architectural design team & check on project fire safety provision?
3.3 | D&B Contract - has there been consultation with Appointed Contactor's M&E / MEP design team & check on project fire safety provision?
4 | Stage 5 (J & K): Implementation (To be reviewed at each stage) |  | Yes | No
4.1 | Has the 'Principle Contractor (PC)' provided a project works fire strategy & fire risk assessment agreed with the UCL Fire Safety Manager ?
4.2 | Mobilisation - prior to starting project works PC decant phasing programming &/or strategy to be agreed and impact mitigation documented with UCL Fire Safety Manager
4.3 | Mobilisation - at site set up & prior to starting works, local fire / safety / fire logistics Toolbox Talk with PC site manager & their safety reps with UCL fire & safety staff
4.4 | Fire Brigade - will fire brigade equipment and facilities be impacted by the works - If YES work through the impact and provide detail / mitigation in project fire risk assessment and fire strategy provision?
4.5 | Fire Brigade - will any rendezvous points for fire services & access to main fire alarm panel been impacted - If YES work through the impact and provide detail / mitigation in project fire risk assessment and fire strategy provision?
4.6 | Fire Brigade - will any fire hydrants be disabled or made inaccessible - If YES work through the impact and provide detail / mitigation in project fire risk assessment and fire strategy provision?
4.7 | Fire Brigade - will any fire service vehicle access be modified, narrowed or blocked - If YES work through the impact and provide detail / mitigation in project fire risk assessment and fire strategy provision?
4.8 | Will any fire fighting / fireman's lifts, dry risers, hose reels, pumps or others be disabled or made inaccessible - If YES work through the impact and provide detail / mitigation in project fire risk assessment and fire strategy provision?
4.9 | Has any Fire Assembly Areas been made smaller or be obstructed by construction compounds? - If YES work through the impact and provide detail / mitigation in project fire risk assessment and fire strategy provision?
4.10 | Is the project going to impact on the operation of existing fire alarm and detection systems, including Emergency Voice Communication (EVC) System; does it have means to raise an alarm with UCL Security Control Room? - If YES work through the impact and provide detail / mitigation in project fire risk assessment and fire strategy provision?
4.11 | Is the project going to generate high fire risks during construction (e.g. highly combustible materials, ignition sources such as hot welding, hazardous processes or storage of hazardous materials, LPG or similar) - If YES work through the impact and provide detail / mitigation in project fire risk assessment and fire strategy provision? (Note - Acetylene is prohibited on site)
4.12 | Escape Routes - will any of the escape routes been impacted (in project building &/or other building stairs & exits etc.) by any works carried out in corridors, stair enclosures, lobbies and vestibules, emergency lighting, that impact on occupants evacuating from the premises safely along these routes? - If YES work through the impact and provide detail / mitigation in project fire risk assessment and fire strategy provision / What arrangements for change process for informing users and other relevant persons of alterations?
4.13 | Escape Routes - will the escape routes from the building (or other buildings) to Fire Assemble areas be made narrower or no longer be available (e.g. through construction vehicle access, waste storage, temporary hoists etc.) - If YES work through the impact and provide detail / mitigation in project fire risk assessment and fire strategy provision?
4.14 | Fire Compartmentation - will any of the fire compartmentation / external fire spread / separating project areas be modified or be impacted on during construction? - If YES work through the impact and provide detail / mitigation in project fire risk assessment internal and external fire spread strategy provision?
5 | Stage 6 (L): Operations (To be reviewed at each stage) |  | Yes | No
5.1 | Regulation 38 (The Building Regulations) - provision of Fire Safety information PRIOR to building occupation by UCL
5.2 | General fire safety inspections - provision of fire extinguishers and fire signage etc.
5.3 | Fire alarm (including EVC / DMS systems / signals back to UCL security control room) - commissioning / UCL fire safety staff to witness
5.4 | Emergency lighting - commissioning
5.5 | Fire brigade equipment and facilities (Fire Lifts / Dry Risers / Smoke Control) - commissioning / UCL fire safety staff to witness
5.6 | Fire brigade equipment and facilities - commissioning / UCL fire safety staff to witness
5.7 | Occupants / staff moving into premises to have initial fire safety familiarisation walk through (MI03)
Completion (signed off by) |  | Project Officer: ………………………………….. Date: …………………………………..
Completion (signed off by) |  | UCL Fire Safety Manager: ………………………………….. Date: …………………..
NOTE - SEPARATE SHEET FOR FIRE SAFETY HANDOVER CHECK SHEET
Documents assisting review to be provided by the central campus team:
> Bloomsbury Campus Masterplan Fire Strategy Report (where appropriate); > All projects - UCL Fire Safety Technical Notes forming part of the Employer's Required (ER's) issued at Stage 3(C) & implemented at Stage 4(D) Design;
Documents to be provided to be provided by the External Project Manager:
Project Phasing layouts indicating: - Marking up of any fire item becoming modified or unavailable; - Any specific mitigation provisions to be put in place to enable UCL to continue occupying their site safety in compliance with the Fire Safety Order; - Availability of the fire alarm and detection systems in public and construction areas; - Temporary escape stairs; - Temporary fire separations; - Fire & safety hoarding provision; - Fire separation from waste and site storage & activities
Completion (signed off by) |  | Project Officer: ………………………………….. Date: …………………………………..

## Fire Safety Handover Checklist
PROJECT FIRE SAFETY REQUIREMENTS - FIRE SAFETY HANDOVER CHECK LIST
UCL Projects (Rev 1 - Oct 2015)
Unique Project Ref: | PS000000
Project Title: | xxxxx
Building Number: | 0
Building: | xxxxx
UCL Project Officer (UPO): | xxxxx
Project Manager (External) / Lead Designer / CDM: | xxxxx
For The Period Up To: | (insert date)
Fire Safety Technical notes available to download from www.ucl.ac.uk/fire/documents
Fire Safety Systems: | Legislation & Standards: | Actioned or Submitted by & Date: | Received by & Date: | Maintenance Responsibility: | Certificates Provided & Stakeholder Approval Confirmed? | Comments / Defects
MEANS OF ESCAPE (MoE): | Fire Safety Order 2005
Escape Routes - are the escape routes from both the space and the premises been walked and found satisfactory? | Fire Safety Order 2005 |  |  | Project & Department | Yes / No / Not Applicable
Escape & Door Furniture - is the door furniture suitable (i.e. emergency type for Places of Assembly, where >60 persons using it etc.) easy to use, lock free where appropriate, suitable for the space/premises use? | Fire Safety Order 2005 |  |  | Project & Department | Yes / No / Not Applicable
Electronic Locks & Barriers - has Gallagher locks and barriers been interface & fitted with emergency release, green box overrides, witnessed & commissioned? | UCL Fire Safety Tech Note TN001 |  |  | Project and Access Systems | Yes / No / Not Applicable
FIRE COMPARTMENTATION: | Fire Safety Order 2005
Fire Doors - are they self-closing, been fitted with strips & seals, 1/2 leaves fitted with self closers, correctly signed, functional & suitable for location, occupants and traffic? | UCL Fire Safety Tech Note TN013 |  |  | Project & Department | Yes / No / Not Applicable
Passive Fire Protection & Fire Stopping - are all penetrations & structural supporting elements suitably fire protected, with a record of works provided? | UCL Fire Safety Tech Note MI06 &TN066 & ADB |  |  | Project & UCL Estates | Yes / No / Not Applicable
Fire Dampers - M&E surveyed and drop check completed? | Approved Document B - Building Regulations |  |  | Project & UCL Estates | Yes / No / Not Applicable
Fire Resisting Shutters - has correct fire rating been provided, is there warning of shutter activation/drop, is there clear markings around drop zone, has it been witnessed & commissioned? | Approved Document B - Building Regulations |  |  | Project & UCL Estates | Yes / No / Not Applicable
Fire Resisting Glazing - has Integrity (& Insulation where necessary) been provided to correct fire rating, and is 'Pyro' etching visible on all glass sheets? | Approved Document B - Building Regulations |  |  | Project & UCL Estates | Yes / No / Not Applicable
Service Risers - constructed to at least FR60 and all penetrations sealed, provided with FD30 doors signed 'fire door keep locked' & fitted with UCL Plant Room Keys? | Approved Document B - Building Regulations |  |  | Project & UCL Estates | Yes / No / Not Applicable
Electrical Switch Cupboards - do they meet FR30 & FD30(S) construction in sleeping accommodation, stairs enclosures & single escape conditions? | Approved Document B - Building Regulations |  |  | Project & UCL Estates | Yes / No / Not Applicable
FIRE ALARM (FA) SYSTEMS: | Fire Safety Order 2005
Fire Alarm System - any alterations and changes to the FA System been witnessed, commissioned & Certs' issued? | BS5839 Series / Fire Safety Tech Note TN54 & TN55 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
l FA Sounder Checks - has the sound pressure levels dB(A) been witnessed & recorded? | BS5839 Series / Fire Safety Tech Note TN54 & TN55 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
l FA Silent Tone Sounders - In BSUs, has Silent Tone sounders been fitted and sound pressure levels dB(A) witnessed & recorded? | BS5839 Series / Fire Safety Tech Note TN54 & TN59* |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
l FA Signal Interfaces - has fire, fault & pre-alarm signals to UCL Security Control (or ARC) been provided? | BS5839 Series / Fire Safety Tech Note TN54 & TN55 |  |  | Access Systems & Estates EM&I | Yes / No / Not Applicable
l FA Access Control Interfaces - on FA Activation has Gallagher controlled doors/barrier release been witnessed? | BS5839 Series / Fire Safety Tech Note TN001 |  |  | Access Systems & Estates EM&I | Yes / No / Not Applicable
l FA Access Control Interfaces - where fire doors fitted with Disabled/MIP opening devices, 'fail closed' on fire alarm activation & witnessed? | BS5839 Series / Fire Safety Tech Note TN002 |  |  | Access Systems & Estates EM&I | Yes / No / Not Applicable
l FA (Other Systems) Interfaces - lifts ground, fire suppression systems, roller shutters or curtains etc. where fitted, work correctly? | BS5839 Series / Fire Safety Tech Note TN54 & TN55 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
l FA FADE signs - where provided, correct locations, witnessed, commissioned & certs issued? | BS5839 Series / Fire Safety Tech Note TN54 & TN58 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
l FA Zones - are Zone Charts & Logbook provided & displayed? | BS5839 Series / Fire Safety Tech Note TN54 & TN55 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
l FA - Deaf Messaging System (DMS) Provided - where provided, witnessed, commissioned & certs issued? | BS5839 Series / Fire Safety Tech Note TN007 / TN54&5 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
EMERGENCY LIGHTING (EL): | Fire Safety Order 2005
Emergency Lighting System - has 3 hr test been completed, witnessed, commissioned & certs issued? | BS5266 Series / Fire Safety Tech Note TN020 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
l If addressable EL system - has a interface to BMS or other control system been provided, witnessed & tested? | BS5266 Series / Fire Safety Tech Note TN020 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
l If none-addressable EL units - has 3 hr test been completed, test keys been installed correctly system witnessed, commissioned & certs issued? | BS5266 Series / Fire Safety Tech Note TN020 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
FIRE BRIGADE EQUIPMENT: | Fire Safety Order 2005
Sprinklers - designed, installed and commissioned with certs issued, has UCL Insurer inspected an approved? | BS END 12845 & LPCB Sprinkler Installation Rules 2009 / TN038 |  |  | Access Systems & Estates EM&I | Yes / No / Not Applicable
Dry Rising & Fire Hydrant Systems - where provide, been witnessed, commissioned & certs issued? | Fire Safety Tech Note TN038 & BS9999 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
Smoke Control & Venting Systems – where provided, been witnessed, commissioned & certs issued? | Fire Safety Tech Note TN038 & BS9999 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
Firefighting Lift Provision - where provided, been witnessed, commissioned & certs issued? | Fire Safety Tech Note TN038 & BS9999 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
Prescribed Voltage Electrical Equipment – where provided, have fireman's switches been witnessed, commissioned & certs issued? | Fire Safety Order 2005 (Article 37) & TN039 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
Fume Cupboards (Fireman's Switch) - where provided have been correctly installed, witnessed, commissioned & certs issued? | UCL Fire Safety Tech Note TN038 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
Containment Level 3 Labs (Fireman's Switch) - where provided have been correctly installed, witnessed, commissioned & certs issued? | UCL Fire Safety Tech Note TN038 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
AHU & Heating Controls - have they been interfaced to close down & auto-restart after fire alarm activation, witnessed & commissioned? | UCL Fire Safety Tech Note TN038 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
FIRE EXTINGUISHERS SYSTEMS: | Fire Safety Order 2005
Portable Fire Extinguishers - correct type provided and installed? | BS5306 Series / Fire Safety Tech Note TN023 |  |  | UCL Fire Safety Manager | Yes / No / Not Applicable
Fire Hose Reels - any works or changes to systems witnessed, commissioned & certs issued? | BS5306 Series / Fire Safety Tech Note TN038 |  |  | UCL Fire Safety Manager & EM&I | Yes / No / Not Applicable
Fire Gas Suppression Systems - any works or changes to systems been witnessed, commissioned & certs issued? | BS5306 Series / Fire Safety Tech Note TN038 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
Fume Cupboard (Fire Suppression) – where provided, has the correct system & been witnessed, commissioned & certs issued? | UCL Fire Safety Tech Note TN038 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
Hypoxic Atmosphere Suppression Systems - any works or changes to systems witnessed, commissioned & certs issued? | BS5306 Series / Fire Safety Tech Note TN038 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
DISABLED / MOBILITY IMPAIRED PERSONS (MIP) FACILITIES: | Fire Safety Order 2005
Disabled Refuges - communications provided witnessed and commissioned | BS 5839-9 / BS9999 / ADB |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
Evacuation Lift Provision - where provided, been witnessed, commissioned & certs issued? | Fire Safety Tech Note TN038 & BS9999 |  |  | Project & UCL Estates EM&I | Yes / No / Not Applicable
FIRE SAFETY SIGNS: | Fire Safety Order 2005
Fire Action Notices (FAN) - provided? | UCL Fire Safety Tech Note TN090 |  |  | UCL Fire Safety Manager | Yes / No / Not Applicable
General Fire Safety Signs - provide? | UCL Fire Safety Tech Note TN090 |  |  | UCL Fire Safety Manager | Yes / No / Not Applicable
FIRE SAFETY STAFF FAMILIARISATION: | Fire Safety Order 2005
Occupying staff - has occupying staff received fire safety familiarisation of the space or building prior to occupation | Fire Safety Order 2005 & Fire Tech Note MI03 |  |  | UCL Project & Fire Safety Managers | Yes / No / Not Applicable
NOTES:

## Revision History (hidden)
Who | Date | Changes
PSO | 2014-06-01 | New template