## Project Header Sheet
UCL CH3 Form
Unique Project Ref: | PS0xxxxx
Project Title :
Building Number (UGC) :
Building Name :
UCL Project Officer (UPO) Name :
Professional Team Approval Date :
Submission Date to Mobilisation & Transition Team :
Version 5.1

## UCL Fire (Major Projects)
PROJECT FIRE SAFETY REQUIREMENTS - PRE-OCCUPATION FIRE SAFETY ASSESSMENT & HANDOVER CHECK LIST
(NOTE - THIS FORM IS TO BE COMPLETED BY UCL FIRE SAFETY TEAM ONLY)
UCL (Major) Projects (Rev 6 - October 2020)
Unique Project Ref: | PSO 0000
Project Title:
Building Number:
Building:
UCL Project Officer (UPO):
Project Manager (External) / Lead Designer / CDM:
For The Period Up To:
Notes on Process & Requirements: | Pre-occupation fire safety assessment - process of identifying fire precautions in a newly constructed or refurbished building, taking into account the approved fire strategy, and deciding whether or not the new or refurbished premises are likely to be fit for occupation. Note the pre-occupation fire safety assessment is not to be confused with the fire risk assessment required by fire safety legislation, which can only properly be carried out after a building has been handed over to the end user.
Signed off by: |  |  |  | Signatures:
Fire Safety Technical Notes available to download from www.ucl.ac.uk/fire
Fire Safety Systems: | Legislation & Standards: | Actioned or Submitted by & Date: | Received by & Date: | Maintenance Responsibility: | Certificates Provided & Stakeholder Approval Confirmed? | Comments / Defects
MEANS OF ESCAPE (MoE): | Fire Safety Order 2005
Escape Routes - are the escape routes from both the project space and the premises have been walked and found to be safe & satisfactory? | Fire Safety Order 2005 |  | 00 May 00
Escape & Doors - is the fire & escape door installation appropriate or suitable for the space/premises use? (i.e. no sliding doors on final exits /places of assembly / opening direction of escape (>60 persons using it / easy to use self closing / latching etc.) | Fire Safety Order 2005 |  | 00 May 00
Electronic Locks & Barriers - has general locks / Gallagher locks / barriers interface & fitted with emergency release, green box overrides, witnessed & commissioned? | UCL Fire Safety Tech Note TN001 |  | 00 May 00
FIRE COMPARTMENTATION: | Fire Safety Order 2005
Fire Doors - are they self-closing, been fitted with strips & seals, 1/2 leaves fitted with self closers, correctly signed, functional & suitable for location, occupants and circulation traffic? | UCL Fire Safety Tech Note TN013 |  | 00 May 00
Fire Resisting Glazing (FRG) - has Integrity (& Insulation where necessary) glazing been provided to correct fire rating and is 'Pyro' etching visible on all glass sheets? | Approved Document B - Building Regulations |  | 00 May 00
Passive Fire Protection & Fire Stopping - are all penetrations & structural supporting elements suitably fire protected, with a record of works provided? | UCL Fire Safety Tech Note MI06 & ADB |  | 00 May 00
Service Risers & Plant Rooms - constructed to at least FR60 (with FD30 doors?) and all penetrations sealed, provided with FD30 doors signed fire door keep locked & fitted with UCL Plant Room locks & keys / Contractors storage and waste removed / Removal of redundant services etc? | UCL Fire Safety Tech Note MI06 & ADB |  | 00 May 00
Electrical Switch Cupboards - do they meet FR30 & FD30(S) construction in sleeping accommodation, stairs enclosures & single escape conditions? | Approved Document B - Building Regulations |  | 00 May 00
Fire Dampers - M&E surveyed and drop check completed? | Approved Document B - Building Regulations |  | 00 May 00
Fire Resisting Curtain / Shutters - has correct fire rating been provided, is there warning of shutter activation/drop, is there clear markings around drop zone, has it been witnessed & commissioned? | Approved Document B - Building Regulations |  | 00 May 00
Fire Dampers - M&E surveyed and drop check completed? | Approved Document B - Building Regulations |  | 00 May 00
FIRE ALARM (FA) SYSTEMS: | Fire Safety Order 2005
Fire Alarm System - any alterations and changes to the FA system have been witnessed, commissioned & Certs' issued? | BS5839 Series / Fire Safety Tech Note TN054 & TN055 |  | 00 May 00
Sounder Checks - has the sound pressure levels dB(A) been witnessed & recorded on drawings? | BS5839 Series / Fire Safety Tech Note TN054 & TN055 |  | 00 May 00
Silent Tone Sounders - have works in BSUs/ AHR been undertaken, if so have Silent Tone sounders been fitted and sound pressure levels dB(A) witnessed & recorded? | BS5839 Series / Fire Safety Tech Note TN054 & TN059* |  | 00 May 00
FA Access Control Interfaces / Signal Back - on FA activation has Gallagher controlled doors/barriers released; and signal been sent &received at UCL control room/ has this been witnessed & by whom? | BS5839 Series / Fire Safety Tech Note TN001 |  | 00 May 00
FA (Other Systems) Interfaces - lifts ground, fire suppression systems, roller shutters or curtains etc. where fitted, work correctly? | BS5839 Series / Fire Safety Tech Note TN054 & TN055 |  | 00 May 00
FADE signs - where provided, correct locations, witnessed, commissioned & certs issued what type? | BS5839 Series / Fire Safety Tech Note TN054 & TN058 |  | 00 May 00
Digital Messaging System (DMS) - where provided, witnessed, commissioned / certs issued - has the Text code and telephone number been passed to fire team? | BS5839 Series / Fire Safety Tech Note TN007 / TN054&5 |  | 00 May 00
FA Zones - are FA Zone Charts provided and mounted in frame / has 'as installed' and 'zone drawings' in .DWG format been provided as part of Reg 38 info? | BS5839 Series / Fire Safety Tech Note TN054 & TN055 |  | 00 May 00
EMERGENCY LIGHTING (EL): | Fire Safety Order 2005
Emergency Lighting System - has 3 hour / blackout test been completed, witnessed, commissioned & certs issued? | BS5266 Series / Fire Safety Tech Note TN020 |  | 00 May 00
Addressable EL system - has a interface to BMS or other control system been provided, witnessed & tested? | BS5266 Series / Fire Safety Tech Note TN020 |  | 00 May 00
None-addressable EL units - has 3 hr test been completed, test keys been installed correctly system witnessed, commissioned & certs issued? | BS5266 Series / Fire Safety Tech Note TN020 |  | 00 May 00
PHOTOVOLTAIC (PV) SYSTEMS: | Fire Safety Order 2005
PVs Monitoring and Maintenance – where installed have proactive monitoring systems to identify faults or maintenance requirements remotely such as ‘SolarEdge’? | FSO Article 38 / Fire Safety Tech Note TN065 |  | 00 May 00
Photovoltaic Installation (Fireman's Switch) - where provided have been correctly installed, witnessed, commissioned & certs issued? Appropriate signage provided. | Fire Safety Order 2005 (Article 37) & TN065 |  | 00 May 00
FIRE BRIGADE EQUIPMENT: | Fire Safety Order 2005
Sprinklers - designed, installed and commissioned with certs issued, has UCL Insurer inspected an approved? | BS END 12845 & LCPL Sprinkler Installation Rules 2009 / TN038 |  | 00 May 00
Dry / Wet Rising & Fire Hydrant Systems - where provide, inspected testing witnessed, commissioned & certs issued - is the signage correct / are all hand wheel valves fitted & tight / securing straps fitted and locked? | Fire Safety Tech Note TN038 & BS9999 |  | 00 May 00
Smoke Control & Venting Systems – where provided, is open protocol, all access and control details been handed to UCL fire team been witnessed, commissioned & certs issued? | Fire Safety Tech Note TN038 & BS9999 |  | 00 May 00
Firefighting Lift Provision - where provided, inspected tested and witnessed, commissioned & certs issued? Instructions provided on use / control changeover etc? | Fire Safety Tech Note TN038 & BS9999 |  | 00 May 00
Prescribed Voltage Electrical Equipment - where provided have firefighter switches been witnessed, commissioned & certs issued? | Fire Safety Order 2005 (Article 37) & TN039 |  | 00 May 00
Fume Cupboards (Firefighter's Switch) - where provided are they correctly installed, connected to the fire alarm witnessed, commissioned & certs issued? | UCL Fire Safety Tech Note TN038 |  | 00 May 00
Containment Level 3 Labs (Firefighter's Switch) - where provided have been correctly installed, witnessed, commissioned & certs issued? | UCL Fire Safety Tech Note TN038a |  | 00 May 00
AHU & Heating Controls - have they been interfaced to close down & auto-restart after fire alarm activation, witnessed & commissioned? | UCL Fire Safety Tech Note TN038 |  | 00 May 00
FIRE EXTINGUISHERS SYSTEMS: | Fire Safety Order 2005
Portable Fire Extinguishers - correct type provided and installed? | BS5306 Series / Fire Safety Tech Note TN023 |  | 00 May 00
Fire Hose Reels - any works or changes to systems witnessed, commissioned & certs issued? | BS5306 Series / Fire Safety Tech Note TN038 |  | 00 May 00
Water Mist Systems - any works or changes to systems been witnessed, commissioned & certs issued? | BS5306 Series / Fire Safety Tech Note TN038 |  | 00 May 00
Gas Fire Suppression Systems - any works or changes to systems been witnessed, commissioned & certs issued? | BS5306 Series / Fire Safety Tech Note TN038 |  | 00 May 00
Fume Cupboard (Fire Suppression) – where provided, has the correct system & been witnessed, commissioned & certs issued? | UCL Fire Safety Tech Note TN038 |  | 00 May 00
Hypoxic Atmosphere Suppression Systems - any works or changes to systems witnessed, commissioned & certs issued? | BS5306 Series / Fire Safety Tech Note TN038 |  | 00 May 00
DISABLED / MOBILITY IMPAIRED PERSONS (MIP) FACILITIES: | Fire Safety Order 2005
MIP - are arrangements in place for Disabled Evacuation? | BS 5839-9 / BS9999 / ADB |  | 00 May 00
Disabled Refuges - communications provided witnessed and commissioned | BS 5839-9 / BS9999 / ADB |  | 00 May 00
Adapted Standard Lift Provision - where provided, been witnessed, has the time out been set, all lift register updated and RA completed commissioned & certs issued? | Fire Safety Tech Note TN038 & BS9999 |  | 00 May 00
Evacuation Lift Provision - where provided, been witnessed, commissioned & certs issued? | Fire Safety Tech Note TN038 & BS9999 |  | 00 May 00
FIRE SAFETY SIGNS: | Fire Safety Order 2005
Fire Safety Signs - are fire door, mean of escape, and general fire / safety signage been provided and installed correctly? | UCL Fire Safety Tech Note TN090 |  | 00 May 00
Fire Action Notices (FAN) - provided? | UCL Fire Safety Tech Note TN090 |  | 00 May 00
FIRE SAFETY INFORMATION & FAMILIARISATION: | Fire Safety Order 2005
Rule 38 (The Building Regulations 2010 ) - has the provision of fire safety information been provided iaw UCL Fire Safety Mandatory Instruction MI05 - relevant to the size & complexity of the works project? | Fire Safety Order 2005 & Fire Tech Note MI03 |  | 00 May 00
Fire Equipment Maintenance PPM (FAMIS /PLANET - Routine) - fire precautions been handed over to DLO for familiarisation & routine testing - fire alarm / sprinklers / smoke curtains & shutters / smoke control / water mist & gas suppressions systems / firefighting & Evac lifts / Emergency Voice Communications Systems (EVCS) etc. | Fire Safety Order 2005 |  | 00 May 00 | UCL Estates DLO Responsibility
Fire Equipment Maintenance PPM (FAMIS/PLANET - Specialist) - fire precautions been handed over to EM&I specialist testing - fire alarm / sprinklers / smoke curtains & shutters / smoke control / water mist & gas suppressions systems / firefighting & evac lifts / Emergency Voice Communications Systems (EVCS) etc. | Fire Safety Order 2005 |  | 00 May 00 | UCL Estates (EM&I) Responsibility
Occupying Staff - has occupying staff received fire safety familiarisation of the space or building prior to occupation as per MI03? | Fire Safety Order 2005 & Fire Tech Note MI03 |  | 00 May 00
NOTES:

## UCL Fire (Small Projects)
PROJECT FIRE SAFETY REQUIREMENTS - PRE-OCCUPATION FIRE SAFETY ASSESSMENT & HANDOVER CHECK LIST
(NOTE - THIS FORM IS TO BE COMPLETED BY UCL FIRE SAFETY TEAM ONLY)
UCL (Small) Projects (Rev 3 - October 2020)
Unique Project Ref: | PSO 0000 / PSN 0000
Project Title:
Building Number:
Building:
UCL Project Officer (UPO):
Project Manager (External) / Lead Designer / CDM:
For The Period Up To:
Notes on Process & Requirements: | Pre-occupation fire safety assessment - process of identifying fire precautions in a newly constructed or refurbished building, taking into account the approved fire strategy, and deciding whether or not the new or refurbished premises are likely to be fit for occupation. Note the pre-occupation fire safety assessment is not to be confused with the fire risk assessment required by fire safety legislation, which can only properly be carried out after a building has been handed over to the end user.
Signed off by: |  |  |  | Signatures:
Fire Safety Technical Notes available to download from www.ucl.ac.uk/fire
Fire Safety Systems: | Legislation & Standards: | Actioned or Submitted by & Date: | Received by & Date: | Maintenance Responsibility: | Certificates Provided & Stakeholder Approval Confirmed? | Comments / Defects
MEANS OF ESCAPE (MoE): | Fire Safety Order 2005
Escape Routes - are the escape routes from both the project space and the premises have been walked and found to be safe & satisfactory? | Fire Safety Order 2005 |  | 00 May 00
Escape & Doors - is the fire & escape door installation appropriate or suitable for the space/premises use? (i.e. no sliding doors on final exits /places of assembly / opening direction of escape (>60 persons using it / easy to use self closing / latching etc.) | Fire Safety Order 2005 |  | 00 May 00
Electronic Locks & Barriers - has general locks / Gallagher locks / barriers interface & fitted with emergency release, green box overrides, witnessed & commissioned? | UCL Fire Safety Tech Note TN001 |  | 00 May 00
FIRE COMPARTMENTATION: | Fire Safety Order 2005
Fire Doors - are they self-closing, been fitted with strips & seals, 1/2 leaves fitted with self closers, correctly signed, functional & suitable for location, occupants and circulation traffic? | UCL Fire Safety Tech Note TN013 |  | 00 May 00
Passive Fire Protection & Fire Stopping - are all penetrations & structural supporting elements suitably fire protected, with a record of works provided? | UCL Fire Safety Tech Note MI06 & ADB |  | 00 May 00
Service Risers & Plant Rooms - constructed to at least FR60 (with FD30 doors?) and all penetrations sealed, provided with FD30 doors signed fire door keep locked & fitted with UCL Plant Room locks & keys / Contractors storage and waste removed / Removal of redundant services etc? | UCL Fire Safety Tech Note MI06 & ADB |  | 00 May 00
Fire Dampers - M&E surveyed and drop check completed? | Approved Document B - Building Regulations |  | 00 May 00
FIRE ALARM (FA) SYSTEMS: | Fire Safety Order 2005
Fire Alarm System - any alterations and changes to the FA system have been witnessed, commissioned & Certs' issued? | BS5839 Series / Fire Safety Tech Note TN054 & TN055 |  | 00 May 00
FA Sounder Checks - has the sound pressure levels dB(A) been witnessed & recorded on drawings? | BS5839 Series / Fire Safety Tech Note TN054 & TN055 |  | 00 May 00
FA Access Control Interfaces / Signal Back - on FA activation has Gallagher controlled doors/barriers released; and signal been sent &received at UCL control room/ has this been witnessed & by whom? | BS5839 Series / Fire Safety Tech Note TN001 |  | 00 May 00
FA (Other Systems) Interfaces - lifts ground, fire suppression systems, roller shutters or curtains etc. where fitted, work correctly? | BS5839 Series / Fire Safety Tech Note TN054 & TN055 |  | 00 May 00
FA Zones - are FA Zone Charts provided and mounted in frame / has 'as installed' and 'zone drawings' in .DWG format been provided as part of Reg 38 info? | BS5839 Series / Fire Safety Tech Note TN054 & TN055 |  | 00 May 00
EMERGENCY LIGHTING (EL): | Fire Safety Order 2005
Emergency Lighting System - has 3 hour / blackout test been completed, witnessed, commissioned & certs issued? | BS5266 Series / Fire Safety Tech Note TN020 |  | 00 May 00
PHOTOVOLTAIC (PV) SYSTEMS: | Fire Safety Order 2005
PVs Monitoring and Maintenance – where installed have proactive monitoring systems to identify faults or maintenance requirements remotely such as ‘SolarEdge’? / Has fire brigade isolation facilities been installed as per TN065? | FSO Article 38 / Fire Safety Tech Note TN065 |  | 00 May 00
FIRE EXTINGUISHERS SYSTEMS: | Fire Safety Order 2005
Portable Fire Extinguishers - correct type provided and installed? | BS5306 Series / Fire Safety Tech Note TN023 |  | 00 May 00
DISABLED / MOBILITY IMPAIRED PERSONS (MIP) FACILITIES: | Fire Safety Order 2005
MIP - are Arrangements in place for Disabled Evacuation? | BS 5839-9 / BS9999 / ADB |  | 00 May 00
FIRE SAFETY SIGNS: | Fire Safety Order 2005
Fire Safety Signs - are fire door, mean of escape, fire action notices been provided and installed correctly? | UCL Fire Safety Tech Note TN090 |  | 00 May 00
FIRE SAFETY INFORMATION & FAMILIARISATION: | Fire Safety Order 2005
Rule 38 (The Building Regulations 2010 ) - has the provision of fire safety information been provided iaw UCL Fire Safety Mandatory Instruction MI05 - relevant to the size & complexity of the works project? | Fire Safety Order 2005 & Fire Tech Note MI03 |  | 00 May 00
Fire Equipment Maintenance PPM (FAMIS /PLANET - Routine) - fire precautions been handed over to DLO for familiarisation & routine testing - fire alarm / sprinklers / smoke curtains & shutters / smoke control / water mist & gas suppressions systems / firefighting & Evac lifts / Emergency Voice Communications Systems (EVCS) etc. | Fire Safety Order 2005 |  | 00 May 00 | UCL Estates DLO Responsibility
Fire Equipment Maintenance PPM (FAMIS/PLANET - Specialist) - fire precautions been handed over to EM&I specialist testing - fire alarm / sprinklers / smoke curtains & shutters / smoke control / water mist & gas suppressions systems / firefighting & evac lifts / Emergency Voice Communications Systems (EVCS) etc. | Fire Safety Order 2005 |  | 00 May 00 | UCL Estates (EM&I) Responsibility
Occupying Staff - has occupying staff received fire safety familiarisation of the space or building prior to occupation as per MI03? | Fire Safety Order 2005 & Fire Tech Note MI03 |  | 00 May 00
NOTES:

## Water Systems
Water Systems Checklist (EM&I)
Water Systems | Received by and Date |  | Comments / Defects
e.g. Water distribution systems, and flushing, cleaning records and chemical dosing certificates? | Main Contractor - xx/xx/xx |  | None
All water hygiene related assets labelled with asset tags by the UCL incumbent water hygiene maintenance contractor?
Water distribution systems, and flushing, cleaning records and chemical dosing certificates?
Chlorination certificate(s) (Dated no less than seven days prior to occupancy)
Water Risk Assessment produced or reviewed and updated?
Copy of notification to local authorities of installation of wet cooling towers and evaporative condensers
Chemical and bacteriological test results for drinking water cisterns greater than 1000 litres
Microbiological examination of water systems – test report
Water hygiene maintenance & inspection regime in place Inc. monthly temperature testing
List of any water features on site that would require management.
Water authority discharge of waste certificate
Source protection policy and licence to use water supplied by a borehole
Has all equipment been demonstrated & necessary staff trained?
Are essential spare parts required?
Water meter readings taken and submitted to UCL?
Water pressure test. Mains Cold Water & District Hot Water
Transition Team |  | Signature |  | Date
Project Officer |  | Signature |  | Date

## Mechanical Systems
Mechanical Systems Checklist (EM&I)
Mechanical Systems | Actioned and/or Submitted by and Date | Received by and Date |  | Comments / Defects
Has an Asset register been produced & all assets labelled with EQ Nos
Heating system test certificates
Pressure systems test certificates
Pressure vessels & systems written schemes of examination
Pipework systems test certificates
Pipework schematics provided and fitted in related plantrooms.
Valves tagged and listed on pipework schematics.
Closed-system chemical analysis reports provided.
Closed systems dosing details.
Gas Appliance and/or Boiler details
Boiler Commissioning data
Seasonal commissioning dates agreed?
Update gas drawing showing appliance loading.
Gas infrastructure drawings amended
Medical gas systems commissioning data (test certification and drawings)
Air compressors commissioning data
Commissioning Manager reviewed all commissioning certification?
Natural gas proving systems tested and certified?
Has all equipment been demonstrated & necessary staff trained? (video clips taken and links added to electronic O&Ms)
All equipment manufacturers and suppliers contained within the O&Ms (Actual equipment used identified?)
Has all pin numbers / codes / passwords/ keys required to gain access to all control panels, panels, BMS systems and all associated items of plant been provided?
Are essential spare parts required?
Gas and/or heat meter – Environmental Sustainability team to be engaged regarding suitable connection is made and the location is known.
Plant replacement strategy document compiled?
Have UCL insurers been advised of additional plant? (Boilers / pressure vessels)
Transition Team |  |  | Signature |  | Date
Project Officer |  |  | Signature |  | Date

## AC & Ventilation
AC & Ventilation Checklist (EM&I)
AC & Ventilation Systems | Received by and Date |  | Comments / Defects
Has an Asset register been produced & all assets labelled with EQ Nos
Air-con system test certificates
Inventory of refrigerants i.e. F-Gas register and details recorded and passed to UCL?
F-gas labels fitted to condensers?
Indoor units fitted with supply ref and condenser ref labels? Condenser units fitted with Indoor units supplied references label. (Traffolyte-type)
Air-con system performance testing results and certificates
Chiller Commissioning data compiled for submission to UCL
Seasonal commissioning dates agreed?
Air conditioning inspection and certification (over 250kw)
Specialised equipment to be defined (i.e. fume cupboards)
Ventilation systems test certificates
Local Exhaust Ventilation commissioning and certification
Commissioning Manager reviewed all commissioning certification?
Identified all Hazardous areas i.e. BSU / Cat 3 Labs
Air tightness test completed (e.g. CL3 Lab)
Confirm all plant tested at full load/volume
Filtration details provided, (sizes, locations, type, AHU, HEPA filters)
Filtration change frequency advised (Where recorded)
Ventilation as-built schematics and air conditioning as-built schematics, placed on relevant plantroom walls?
Supplier warranty and maintenance details of service level agreements
All planning restrictions discharged? i.e.- acoustic requirements
Has all equipment been demonstrated & necessary staff trained? (video clips taken and links added to electronic O&Ms)
All equipment manufacturers and suppliers contained within the O&Ms (Actual equipment used identified?)
Has all pin numbers / codes / passwords/ keys required to gain access to all control panels, panels and all associated items of plant been provided?
Are essential spare parts required?
Transition Team |  | Signature |  | Date
Project Officer |  | Signature |  | Date

## BMS
BMS (EM&I)
BMS Control Systems | Received by and Date |  | Comments / Defects
Has an Asset register been produced & all assets labelled with EQ Nos (at outstations)
BMS demonstrated to be connected to UCL 'Head End'.
Have graphics been set up and proved? Screenshots provided showing 'fault-free' at Stage Gate 5b.
BMS strategy document provided and embedded within the main screen page of the BMS?
BMS front end software updated and time schedules set
Have all links using the ISD system been proved & witnessed?
Alarm list created, critical alarms and actions agreed.
Any departmental-managed equipment connected to BMS system? (alarm monitoring)
Lighting control system programmed and operational
Have any software licences been handed over?
Training session to be arranged with UCL maintenance team to fully demonstrate the whole BMS system
Has all equipment been demonstrated & necessary staff trained? (video clips taken and links added to electronic O&Ms)
Has all pin numbers / codes / passwords/ keys required to gain access to all control panels, panels and BMS computer systems?
Are essential spare parts required?
Transition Team |  | Signature |  | Date
Project Officer |  | Signature |  | Date

## Lifts
Lifts Checklist (EM&I)
Lifting Systems | Received by and Date |  | Comments / Defects
Has an Asset register been produced & all assets labelled with EQ Nos?
Lift installation type test certificates for locking devices, governors, buffers and doors.
Lift installation test certificates received?
Lift maker’s high voltage test certificates received?
Log book & keys issued to maintenance contractor, annual PTW raised by UPO?
Has lift maintenance programme been arranged by UPO?
Has all pin numbers / codes / passwords/ keys required to gain access to all control panels, panels and all associated items of plant been provided?
Lift shaft, ropes, guides and ropes all confirmed to have been cleaned down prior to handover?
Lifting equipment reports of thorough examination provided?
Lift emergency call system hard-wired back to UCL security and tested / confirmed operational?
Lift numbered to UCL system, permanent labels fitted? (COP, lift car & landing doors)
Lift controllers or head-end PC demonstrated and set to log all lift failure incidents?
Adequate shaft ventilation? Cooling within the Lift Motor Room provided, if required?
Has all lifting equipment been demonstrated & necessary staff trained?
Lift pit access arrangements confirmed to be sufficient?
Lifting Beams -Asset-tagged? Maintenance procedure defined?
Arjo hoist demonstrated and maintenance regime set up. Thorough examinations programmed and equipment registered?
Lifting equipment reports of thorough examination?
Have UCL insurers been advised of additional Lifts?
Escalator test certificate received?
Escalator reports of thorough examination received?
Are essential spare parts required?
Transition Team |  | Signature |  | Date
Project Officer |  | Signature |  | Date

## Electrical Systems
Electrical Systems Checklist (EM&I)
Electrical Systems | Received by and Date |  | Comments / Defects
Has an Asset register been produced & all assets labelled with EQ Nos?
Electrical test certificates provided?
Emergency lighting details & test results completed and certificates submitted?
Generator test and commissioning data provided?
UPS test and commissioning data?
Commissioning Manager reviewed all commissioning certification?
High level lighting details & lux level test results completed and submitted to UCL?
Street lighting lux level tests and ballast selection calculations included?
Lightning protection system design details and test certificates provided?
PV (solar) generation certified and maintenance strategy defined?
Records of tests carried out on used electrical appliances?
Switchgear manufacturers certificates provided?
PA systems commissioned?
Meter connection to UCL’s EMON system arranged through EM&I?
Electrical infrastructure drawings and/or amended?
Electrical schematic drawings fitted?
Plant replacement strategy document completed and added to O&Ms?
Has all equipment been demonstrated & necessary staff trained (separate training and familiarisation sessions arranged)
Video clips taken of training sessions and added to electronic copy of O&Ms?(Links provided?)
All equipment manufacturers and suppliers information contained within the O&Ms? (Actual equipment installed identified?)
Has all pin numbers / codes / passwords/ keys required to gain access to all control panels, boards and all associated items of electrical equipment been provided?
Are essential spare parts required? (spares collected and protected in manufacturers packaging and safely stored)
Transition Team |  | Signature |  | Date
Project Officer |  | Signature |  | Date

## Building Fabric
Building Fabric Checklist (EM&I)
Building Fabric | Received by and Date |  | Comments / Defects
Has an Asset register been produced & all assets labelled with EQ Nos
Building control/building regulations signed off?
Attain declaration relating to asbestos presence within the building and modify Asbestos Register.
Has Asbestos Register been updated?
Update Asbestos Database inc CAD drawings.
DWG drawings sent to CAD Team to update floor plans?
Drainage system test certificates received?
Drainage survey undertaken and video provided at handover?
Drainage infrastructure drawing amended?
Automatic door commissioning certification? Maintenance programmed?
Roof access satisfactory?
Update Roof survey database
Gutter cleaning carried out?
Tiered seating inspection.
Moveable wall inspection.
Provision of finishes schedule i.e. decoration, floor finish, ceilings etc.
Details of utility hole covers/access ways etc.
Video clips taken of training sessions and added to electronic copy of O&Ms (Links provided?)
Essential spare parts list for site stores
Provide copy of building fabric snagging list.
Transition Team |  | Signature |  | Date
Project Officer |  | Signature |  | Date

## Facilities
Facilities Checklist (F&I)
Facilities Systems | Received by and Date |  | Comments / Defects
Did outgoing department provide all necessary decontamination certification and all chemicals disposed of in the correct manner?
Has a full builders/sparkle clean been completed and the building fit for occupation?
Has the Soft Services Manager been informed to commence/re-commence cleaning/waste disposal regime?
Provided cleaning strategy to Soft Services Manager?
Have windows been cleaned and cleaning methodology demonstrated?
Flooring correctly sealed, all information and training on floor cleaning and maintenance detailed within the O&Ms?
Has all equipment been demonstrated to end users and third party maintenance contractors & necessary staff trained?
Training sessions and technical equipment operations recorded by video and incorporated within the O&Ms?
Disabled access, special treatment considered (e.g. gritting + salt box)
Copy of the roads and car parks design and surface area m2 for gritting provided?
Landscape design plan for the site to scale. 1:200 is the preferred scale, in accordance with the UCL Bio-diversity plan.
Topographical survey data in respect of slopes - mowing provided?
Any tree pruning/maintenance requirement?
List of Tree Preservation Orders
Transition Team |  | Signature |  | Date
Project Officer |  | Signature |  | Date

## Security
Security Checklist
Security Systems | Received by and Date |  | Comments / Defects
Has an Asset register been produced & all assets labelled with EQ Nos?
Security alarm test certificates (intruder / panic alarm) confirming action to set and reset is fully functioning?
Access control system installation certification and witnessed UCL Security?
CCTV system test certificates provided? Has the system been witnessed by the UCL Security team?
Confirmation that the intercom system has been witnessed, certified and is operational?
Confirmed disabled access installations demonstrated, certified and training given?
Is the area / building confirmed to be capable of being secured as specified. If not then staffing contingency made until it is secured
Have all head-end systems been programmed correctly with site plans etc.?
Access control system programming confirmed as complete, system plans updated to match the new system?
Handover access arrangements agreed with permits as required?
Have arrangements been made with UCL Security to attend the physical handover of the space?
Snagging list compiled and handed to UPO for addition to defects list
Has all equipment been demonstrated & necessary staff trained?
Have keys/cards that have been issued to the contractor been returned?
Has the keys/PIN numbers/passwords/access codes for the new installation and equipment been handed over?
Have all UCL supplied master key locks been confirmed as fitted?
Has all RADAR keys for Changing Places facilities been provided to UCL Security?
Have as-built system drawings been submitted to UCL security in both PDF / DWG electronic file format?
Essential spares provided?
Transition Team |  | Signature |  | Date
Project Officer |  | Signature |  | Date

## Utilities & Sustainability
Utilities and Sustainability (ES) Checklist
Utilities & Sustainability | Received by and Date |  | Comments / Defects
All actions and information relating to points for BREEAM / Ska / MiniSka ratings submitted?
Has a building user guide been provided, as per UCL Standard?
Energy design calculations achieved / information for DEC’s / EPC’s?
Environmental certification issued and displayed? (where applicable)
Details of any gas, electric and/or water meters removed, installed or replaced provided to the Sustainable UCL team? (including reference, MPAN, MPRN, location on building plan)
Incumbent utility provider notified of meter changes where used for billing purposes?
All meters linked to BMS? (proven operational)
Details of any incumbent utility supplier been provided to the Sustainable UCL team? NO NEW CONTRACTS TO BE AGREED
End/start of supply readings been taken and provided?
Meter readings for all utilities taken and provided monthly for 1 year following handover?
Site Waste Management Plan confirms application of waste hierarchy on site?
Waste volume, type and method of disposal recorded and provided to the Environmental Sustainability team
Has appropriate signage been provided to ensure that building users know how to operate elements of the building, e.g. lighting and HVAC controls?
Training sessions arranged and guides provided on use of the various software systems?
Commissioning data for all renewables provided?
Has energy data been added to Carbon Buzz for all new builds and any major refurbishments?
Number of cycle parking spaces available to new building users provided to the Sustainable UCL team?
Transition Team |  | Signature |  | Date
Project Officer |  | Signature |  | Date

## Miscellaneous
Miscellaneous Checklist (EM&I)
Miscellaneous Systems | Received by and Date |  | Comments / Defects
Has an Asset register been produced & all assets labelled with EQ Nos?
H&S File and O&Ms signed off by Professional Team/PM and in agreed UCL format?
Soft Landings Template completed and submitted?
Maintenance strategy compiled into a single document?
All gender-neutral toilets listed on UCL Toilet Map?
All signage in accordance with UCL Signage Guide Manual?
Fall arrest system – maintenance / inspection regime?
Fall arrest systems – LOLER inspection carried out and certified?
Confined Spaces – Safe system of work provided?
Changing Places tables maintenance agreed with EM&I?
All planning conditions discharged?
Noise assessment management records and noise limits complied with as per planning consents?
COSHH Assessments and Product Data Sheets for any hazardous materials handed over?
Maintenance responsibility established for Green / Brown Roofs.
Building services operating and maintenance information including emergency procedures?
Risk assessment records for plant and systems?
Documentation for Wayleaves and adopted roads
Contractor to compile a list of handover items to be passed to UCL
Documentation regarding any special designation ‘Conservation Area’
Transition Team |  | Signature |  | Date
Project Officer |  | Signature |  | Date

## Departmentally Managed Equip
Departmentally Managed Equipment Checklist (EM&I)
Miscellaneous Systems | Received by and Date |  | Comments / Defects
Has an Asset register been produced & all assets labelled with EQ Nos?
Departmentally managed equipment identified?
Department's responsibility regarding statutory compliance and maintenance explained and understood by users?
FAMIS and Crimson updated for eligible equipment?
Has equipment been demonstrated to Department by users?
Has all equipment been demonstrated & necessary staff trained? (video clips taken and links added to electronic O&Ms)
H&S File and O&Ms provided to Departmental Safety Officer/ Lead Equipment user?
Transition Team |  | Signature |  | Date
Project Officer |  | Signature |  | Date

## Outstanding Defects
Outstanding Defects/ Day Two Works (Contractor)
Item |  | Action Required to Rectify Defect | Defect Rectification Responsibility by Whom? | Anticipated Date of Completion |  | Actual Completion Date | Comments
Defect
e.g. Compressor Air Cylinder | Pressure Gauge cannot be seen by operatives | Turn gauge so it can be seen | Main Contractor (XX Ltd) | xx/xx/xxxx |  | xx/xx/xxx
Transition Team |  |  |  |  | Signature |  | Date
Project Officer |  |  |  |  | Signature |  | Date

## Cat list (hidden)
Certificates Provided & Stakeholder Approval Confirmed? | Signed off by: | Signatures: | Actioned or Submitted by & Date: | Maintenance Responsibility - Post PC: | Maintenance Responsibility:
Yes | Simon Cooke | Simon Cooke | UCL Fire Team (SC) | Defects - Principal Contractor | Capital Projects (Latent Defects)
Yes With Comments | Michael Said | Michael Said | UCL Fire Team (MS) | Principal Contractor | Department (Day to Day)
No | Dan Murray | Dan Murray | UCL Fire Team (DM) | Estates (EM&I) | Landlord
Not Applicable |  |  |  | Estates (DLO) | Security / Access Systems
|  |  |  | Estates (Security) | UCL Estates DLO Responsibility
|  |  |  | Estates (Fire Safety) | UCL Fire Safety Manager
Yes / No / Not Applicable |  |  |  | Department | UCL Estates (EM&I) Responsibility
Principal Contractor (Warranty & Latent Defects)