## Equipment & Activity Checklist
Appendix 1: Seasonal Commissioning - Checklist of Systems to be Assessed
Project:
Checklist completed by:
RIBA Stage:
Date:
Number of seasonal commissioning sessions required:
Introduction:
This appendix includes a checklist of all the systems and data points to be monitored across each season for seasonal commissioning. Ahead of tender, the building services consultant shall complete this checklist by identifying which systems, data parameters and activities are to be included within the scope of works, agreeing this in advance with the UCL Estates Mobilisation and Transition team. The completed checklist shall form part of the seasonal commissioning scope of works for the contractor and shall be included within the tender package. All BMS data points listed below are to be monitored for a minimum of 2 weeks ahead of each seasonal commissioning session wherever possible.
Equipment & Activities | Within Scope of Project? (Consultant to confirm)
Mechanical
Air Handling Units
Monitor the following parameters / trend logs to assess performance against design specifications:
· Outdoor air, supply air, return air temperatures
· Air flow rates via BMS
· LTHW / CHW valve positions
· Set points
· Fan speed (% of max load)
· Pressure readings
· CO2 levels (if applicable)
· Other
Additional checks:
· Can supply air temperature be optimised to reduce the number of terminal units reheating cool supply air from the AHUs? And vice versa to reduce the number of terminal units cooling warm supply air? Any changes to set points to be approved by Mechanical building services consultant.
For heat recovery unit operation:
· Monitor outdoor air temperature, return temperature, supply temperature, exhaust air temperature to check heat recovery unit is operating well under correct temperature conditions
· Pump speed for run around coils (% of max)
Air Source / Ground Source Heat Pumps
Monitor the following parameters / trend logs to assess performance against design specifications:
· LTHW / CHW flow and return temperatures
· LTHW / CHW flow rates
· Set points
· Run hours
· Outdoor air temperature
· Borehole side water temperatures
· Pump speed (as % of max)
· Other
Additional checks:
· Borehole side of ground source heat pump achieving a thermal energy balance across the year? Provide trend logs to evidence this.
· Can set points be adjusted to improve performance and reduce energy consumption? Any changes to set points to be approved by Mechanical building services consultant.
Boilers & Pumps
Monitor the following parameters / trend logs to assess performance against design specifications:
· LTHW flow and return temperatures
· LTHW flow rates
· Set points
· Run hours
· Other
Additional checks:
· Can set points be adjusted to improve performance and reduce energy consumption? Any changes to set points to be approved by Mechanical building services consultant.
Chillers & Pumps
Monitor the following parameters / trend logs to assess performance against design specifications:
· CHW flow and return temperatures
· CHW flow rates
· Set points
· Run hours
· Outdoor air temperature
· Other
Additional checks:
· Can set points be adjusted to improve performance and reduce energy consumption? Any changes to set points to be approved by Mechanical building services consultant.
Condensers (for VRF and DX systems)
· Run hours
· Time schedules
· Heating and cooling mode schedules
Comms Room DX Splits
Monitor the following parameters / trend logs to assess performance against design specifications:
· Supply air temperature
· Return air temperature
· Room temperature
· Set points
· Run hours
District heating connection / Heat exchanger connections
Monitor the following parameters / trend logs to assess performance against design specifications:
· Primary and Secondary LTHW / CHW temperatures
· Primary and Secondary LTHW / CHW flow rates
· Set points
· Control valve positions
· Heat meter readings (kWh)
· Other
Fan Coil Units / Chilled Beams / Radiators / Other water-based terminal heating or cooling units
Monitor the following parameters / trend logs to assess performance against design specifications:
· LTHW / CHW flow and return temperatures
· Space temperatures - are we achieving set points in each space and we able to achieve these within a reasonable time frame?
· CHW / LTHW control valve positions
· Set points
· Fan speed
· Other
Additional checks:
· Are CHW and LTHW control valves opening simultaneously or within 15 minutes of each other?
· Check the operation of systems to ensure there is no conflict of systems such as heating and cooling of spaces simultaneously, or any conflicts between newly installed systems and existing systems (e.g. conflict between newly installed FCUs with existing radiators)
· Are set points in line with UCL heating and cooling policy?
· If fresh air is ducted to the back of FCUs, are FCU fans running even when there is no demand for heating or cooling to ensure that fresh air is being supplied into the space? This should be compared against design specification.
· Compare any issues highlighted by occupants against BMS log
· Can set points be adjusted to improve performance and reduce energy consumption? Any changes to set points to be approved by Mechanical building services consultant.
Humidifiers
Monitor the following parameters / trend logs to assess performance against design specifications:
· Relative humidity upstream of humidifier
· Set points
· Run hours
Mechanical Ventilation Heat Recovery Units
Monitor the following parameters / trend logs to assess performance against design specifications:
· Supply air, outdoor air, return air, exhaust air temperatures
· Set points
· Bypass position
· Run hours
· LTHW valve position
· CO2 levels of room served
· Other
Natural Ventilation
For naturally ventilated spaces, review the following parameters to assess performance against design specifications:
· Review temperatures and thermal comfort of room, can take live measurements if no sensors in room
· Review indoor air quality (e.g. CO2 levels)
· Review occupant feedback
· Review window contact sensor operation and whether this is working effectively with controls strategy
· Other
Pumps and fans
Monitor the following parameters / trend logs to assess performance against design specifications:
· Run hours
· Pump speed / fan speed (are fan and pump speeds typically operating at efficient speeds according to their specific pump and fan curves?)
· Other
Solar Shading / Automatic control of blinds
· Correct functionality of automatic controls?
· Are shades being used as intended? (e.g. down in the summer, up in the winter, prevention of glare)
VAVs / CAVs
Monitor the following parameters / trend logs to assess performance against design specifications:
· Supply air temperature
· Space temperatures - are we achieving set points in each space and we able to achieve these within a reasonable time frame?
· Air flow rates
· LTHW control valve position
· Indoor air quality (e.g. CO2 levels)
· Set points
· Run hours
· Other
VRF and Split Systems (indoor units)
Monitor the following parameters / trend logs to assess performance against design specifications:
· Supply air temperature
· Return air temperature
· Room temperature
· Run hours
· Time schedules
· Heating and cooling mode schedules / Summer & Winter Modes
Metering Systems
· Check that the following on-site meters and sub-meters are reading and logging data correctly, and are labelled correctly:
o Main utility meters (electricity, gas, district heating network, water)
o Renewable energy systems (e.g. solar PV)
o Electrical sub-meters
o Heat / DHW sub-meters
o Others
· Check that the following remote energy management systems are reading and logging data correctly, and are labelled correctly:
o EMON
o Demand Logic
o Fabriq
o Solar Edge
o Other
Building Management System and Controls
· Check time schedules of plant are still suitable for building use. Can these be optimised to reduce energy consumption whilst retaining high levels of comfort and system performance?
· Optimise heating & cooling start up regimes / morning boost modes. Can the duration of these periods be reduced to minimise the duration of energy-intensive use whilst retaining high levels of comfort and system performance?
· Are set points still in line with design specifications? Can any set points be adjusted to improve energy efficiency? (Deviations from design specifications to be approved by building services consultant)
· Can deadbands be optimised to improve performance and / or reduce energy consumption whilst retaining high levels of comfort?
· Check whether sequencing of operation of components is suitable.
· Optimise control loops where necessary
· Monitor hand status on equipment to ensure plant is operating in auto and in line with design specifications
· Check through log of faults / alarms.
· Adjust location of sensors if necessary to ensure accuracy in readings
· Other
Electrical
Daylight dimming
· Is target lux level appropriate? Any changes to set points to be approved by Electrical building services consultant.
· Are we achieving correct lux levels in space at different times of the day?
Other
Building Services consultant to list other parameters to be monitored as part of seasonal commissioning below: